## Sheet1
Calculating the DSR ceiling price relative to the lowest cost investment alternative
| Discount rate | 4%
| Investment to be deferred (£m) | 1.5
| DSR contract period (yrs) | 5
| MW demand reduction required to defer investment through DSR contract period (MW) | 2
| Set-up costs (£m) | 0.1
| Ongoing operating costs | 5%
| Confidence | 75%
| DSR availabilty window (days/yr) | 83
| yr | 0 | 1 |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
| Main investment (deferred) - £m | 0 | 0 |  | 0 | 0 | 0 | -1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DSR set-up costs - £m | -0.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net cashflows (exc ongoing operating costs) - £m | -0.1 | 0 |  | 0 | 0 | 0 | -1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annual value of deferred investment - £m | 0 | -0.049053 |  | -0.049053 | -0.049053 | -0.049053 | -0.049053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -0.1 |  | 0 | 2: -0.049053; 3: -0.049053; 4: -0.049053; 5: -1.5491; 6: 0; 7: 0; 8: 0; 9: 0
-1.4462
| DSR ceiling (£k/MW-year) | 17.4751 | k
| DSR ceiling (£/MW-day) | 210.5429
| or (£k/MWh) | 2.1844 | k
| MW required to be contracted | 2.6667
NOTES 1. Cost up the conventional solution, to give a figure in £m: guide value £1.5m (replacing two primary transformers by larger units, plus ancillary works) 2. Cost up the provision of a DSR controller at the relevant substation, and the work required to find DSR providers, draw up contracts, and set up payment arrangements, to give a figure for set-up costs in £m: guide value £0.1m 3. Calculate the amount of demand reduction required to defer that investment by five years, to give a figure in MW: guide value 2MW 4. Draw up an NPV at the regulatory discount rate (guide value 4%) to derive an annual benefit of deferral (see attached spreadsheet): guide value comes out at £49k 5. Divide this by the MW required to give a £/MW-yr value: guide value comes out at £24k5 6. Reduce this figure to reflect ongoing operating, monitoring and administrative costs: guide value 5% 7. Reduce this figure to reflect confidence in service provision (and hence over-contracting required): guide value 75% 8. Divide this by the required availability window: guide value 83 days, giving £211/MW-day contracted a. For reference purposes, assuming 8hrs/yr typical utilisation, this is north of £2,000/MWh 9. Go to tender and, if the required firm capacity can be found with an average price below this ceiling, contract for DSR: otherwise, go for a network solution 10. Pay the availability charge, recognising this as an operating cost 11. If the provider fails to deliver, claw back any payments made
Author Dave Miller , Northern Powergrid
Copyright Northern Powergrid (Northeast) Limited. Northern Powergrid (Yorkshire) plc, 2014.
Note on C7: Regulatory discount rate
Note on C8: Cost of the lowest cost alternative solution
Note on C9: Number of years that the investment can be deferred based upon forecast load growth rates
Note on C10: The amount of demand reduction required to defer that investment by five years
Note on C11: The fixed costs of providing a DSR controller at the relevant substation plus the work required to find DSR providers, draw up contracts, and set up payment arrangements.
Note on C13: Reliability of DSR (Used to calculate how much DSR would need to be purchased in order to deliver the capacity required.
Note on C14: Availability window. i.e the number of weekdays during the period of peak loading (i.e. thereare 83 weekdays between November and February)
Note on B20: Value of deferring the capex by x years after taking into account the DSR setup costs
Note on C25: Equals the Value of deferred investment a) reduced by 5% to allow for ongoing operating costs, b) multiplied by the reliability to reflect the overpurchase requirements and c) divided by the capacity required to give a £/MW.
Note on C27: Divide Rate/MW/yr by the days in the availability window to give a ceiling for the rate per day
Note on C29: or divide by the hours per year to give a rate per MWh contracted
Note on C31: This is equal to the actual DSR requirement divided by the confidence factor