## RTTR_EHVHV_UG
Solution Overview | Representative Solution: | RTTR |  |  |  | Smart Variant | discount rate | 3.5%
| Variant Solution: | RTTR for EHV/HV UG cables |  |  |  |  | Y1 | 0 | 0 | 0 | annual opex (per feeder)
| Description: | The use of measurement and ambient forecasting data to predict the rating (and hence current carrying capacity) of assets in a real-time mode. This variant considers RTTR for EHV underground cable circuits. |  |  |  |  | y2 | 500 | 0 | 0
|  | EHV | HV | LV | Comments |  | Y3 | 500 | 0 | 0
Headroom Release (%) | Thermal Cable: | 0% | !% | !% | CLNR has found that there is no potential for improving the ratings at EHV or HV versus P17 ratings |  | Y4 | 500 | 0 | 0
| Thermal Transformer: | 0% | !% | !% | No expected benefit |  | Y5 | 500 | 0 | 0
| Voltage Head: | 0% | !% | !% | No expected benefit |  | Y6 | 500 | 0 | 0
| Voltage Leg: | 0% | !% | !% | No expected benefit |  | Y7 | 500 | 0 | 0
| Power Quality: | 0% | !% | !% | No expected benefit |  | Y8 | 500 | 0 | 0
| Fault Level: | 0% | !% | !% | No expected benefit |  | Y9 | 500 | 0 | 0
Cost (£) | Capital: | 55000 |  |  | Estimate based on the purchase and installation of monitoring devices at key points along the underground cable. This cost is high on the assumption that as cables are a high value asset, that are permenantly damaged by thermal stressing, additional monitoring would be required along their length. Excavation to place monitoring devices next to, or on, the cable are also considered, further increasing the cost. Assuming the average EHV circuit is 4km, with monitoring and communications at every 0.5km of c£6k each. It is noted that this cost does appear high, and would value further evidence to support the true costs of real installations |  | Y10 | 500 | 0 | 0
| Operational Expenditure: | 0 |  |  | No ongoing opex cost assumed (NB. Costs of weather monitoring are factored into the associated Enabler) |  | Y11 | 500 | 0 | 0
| NPV of Opex: | 0 |  |  | Based on 20 year of annual operating expenditure @ 3.5% discount rate |  | Y12 | 500 | 0 | 0
| Cost Curve Type: | 3 |  |  | Assume a reduction in costs as solution volumes increase |  | Y13 | 500 | 0 | 0
| Life Expectancy of Solution: | 15 |  |  | At present, asset life is something of an unknown. The equipment is designed to act in a “fit and forget” manner without the requirement for ongoing maintenance. The life of the equipment for undergroud cable thermal ratings solutions (i.e. thermocouples, RTDs, etc.) is assumed to be 15 years; |  | Y14 | 500 | 0 | 0
| Totex (£): | 55000 |  |  | Calculated from capex plus NPV of opex |  | Y15 | 500 | 0 | 0
Merit Order | Disuption Factor (1-5): | 2 |  |  | Low disruption as the devices can be connected to the network with minimal of impact / outages |  | Y16 | 500 | 0 | 0
| Disruption Cost (£): | 2500 |  |  | Figure based on Disruption Factor (taken from Table 13.7 in the WS3 Report) |  | Y17 | 500 | 0 | 0
| Flexibility (1-5): | 4 |  |  | Devices could easily be moved from one circuit to another within their life expectancy |  | Y18 | 500 | 0 | 0
| Lead Time | 6 |  |  | Typically 6 months lead time for acquisition
| Cross Network Benefits Factor: | 0 |  |  | No benefit expected |  | Y19 | 500 | 0 | 0
Other Benefits | Impact on Fixed Losses (%): | 0% |  |  | No benefit expected |  | Y20 | 500 | 0 | 0
| Impact on Variable Losses (%): | 10% |  |  | Solution is expected to increase the variable losses (I²R) as more current is pushed down the circuit. The exact increase depends on the magnitude and duration of operating at these higher currents.
| Impact on quality of Supply (%): | 1% |  |  | A marginal benefit to QoS as this solution may provide additional monitoring of the network, potentially assisting DNOs in identifying faults or fault locations.
Year solution is available: |  | ? |  |  | Based on CLNR learning we would not currently deploy this solution
Year data (on soln) is available: |  | ? |  |  | Based on CLNR learning we would not currently deploy this solution
Source of Data: |  | CLNR, Workstream 2
Smart Solution Relevance (WS3 Ph1) | Smart Solution Set: | Smart D-Networks 3
| Focus: | Plant & Systems reliability, failure mode detection
| Subset: | Dynamic ratings for all plant types and multi element circuits

## RTTR_LV_UG
Solution Overview | Representative Solution: | RTTR |  |  |  | Smart Variant | discount rate | 3.5%
| Variant Solution: | RTTR for LV UG cables |  |  |  |  | Y1 | #REF! | 0 | 0 | annual opex (per feeder)
| Description: | The use of measurement and ambient forecasting data to predict the rating (and hence current carrying capacity) of assets in a real-time mode. This variant considers RTTR for LV underground cable circuits. |  |  |  |  | y2 | 500 | 0 | 0
|  | EHV | HV | LV | Comments |  | Y3 | 500 | 0 | 0
Headroom Release (%) | Thermal Cable: | !% |  | 5% | Whilst ratings are site specific, they could be enhanced by perhaps 10% dependent upon the difference between the actual load profile and the profile of Engineering Recommendation P17 – ‘Load Curve G’ (Loss Load Factor = 5.061). It should be noted that the rating enhancement for underground cables is likely to be considerably less than that available via applying dynamic ratings to overhead lines. We assume that the use of dynamic thermal rating has no impact on the degradation of the primary assets (the overhead lines, underground cables or transformers), i.e. no accelerated ageing. |  | Y4 | 500 | 0 | 0
| Thermal Transformer: | !% |  | 0% | No expected benefit |  | Y5 | 500 | 0 | 0
| Voltage Head: | !% |  | 0% | No expected benefit |  | Y6 | 500 | 0 | 0
| Voltage Leg: | !% |  | 0% | No expected benefit |  | Y7 | 500 | 0 | 0
| Power Quality: | !% |  | 0% | No expected benefit |  | Y8 | 500 | 0 | 0
| Fault Level: | !% |  | 0% | No expected benefit |  | Y9 | 500 | 0 | 0
Cost (£) | Capital: | 26000 |  |  | Estimate based on the purchase and installation of monitoring devices at key points along the underground cable. This cost is high on the assumption that as cables are a high value asset, that are permenantly damaged by thermal stressing, additional monitoring would be required along their length. Excavation to place monitoring devices next to, or on, the cable are also considered, further increasing the cost. Assuming the average HV circuit is 5km, with monitoring and communications at every 1km of c£5k each. It is noted that this cost does appear high, and would value further evidence to support the true costs of real installations |  | Y10 | 500 | 0 | 0
| Operational Expenditure: | 0 |  |  | No ongoing opex cost assumed (NB. Costs of weather monitoring are factored into the associated Enabler) |  | Y11 | 500 | 0 | 0
| NPV of Opex: | 0 |  |  | Based on 20 year of annual operating expenditure @ 3.5% discount rate |  | Y12 | 500 | 0 | 0
| Cost Curve Type: | 3 |  |  | Assume a reduction in costs as solution volumes increase |  | Y13 | 500 | 0 | 0
| Life Expectancy of Solution: | 15 |  |  | At present, asset life is something of an unknown. The equipment is designed to act in a “fit and forget” manner without the requirement for ongoing maintenance. The life of the equipment for undergroud cable thermal ratings solutions (i.e. thermocouples, RTDs, etc.) is assumed to be 15 years; |  | Y14 | 500 | 0 | 0
| Totex (£): | 26000 |  |  | Calculated from capex plus NPV of opex |  | Y15 | 500 | 0 | 0
Merit Order | Disuption Factor (1-5): | 2 |  |  | Low disruption as the devices can be connected to the network with minimal of impact / outages |  | Y16 | 500 | 0 | 0
| Disruption Cost (£): | 2500 |  |  | Figure based on Disruption Factor (taken from Table 13.7 in the WS3 Report) |  | Y17 | 500 | 0 | 0
| Flexibility (1-5): | 4 |  |  | Devices could easily be moved from one circuit to another within their life expectancy |  | Y18 | 500 | 0 | 0
| Lead Time | 6 |  |  | Typically 6 months lead time for acquisition
| Cross Network Benefits Factor: | 0 |  |  | No benefit expected |  | Y19 | 500 | 0 | 0
Other Benefits | Impact on Fixed Losses (%): | 0% |  |  | No benefit expected |  | Y20 | 500 | 0 | 0
| Impact on Variable Losses (%): | 10% |  |  | Solution is expected to increase the variable losses (I²R) as more current is pushed down the circuit. The exact increase depends on the magnitude and duration of operating at these higher currents.
| Impact on quality of Supply (%): | 0.01% |  |  | A marginal benefit to QoS as this solution may provide additional monitoring of the network, potentially assisting DNOs in identifying faults or fault locations.
Year solution is available: |  | ? |  |  | Based on CLNR learning we would not currently deploy this solution
Year data (on soln) is available: |  | ? |  |  | Based on CLNR learning we would not currently deploy this solution
Source of Data: |  | CLNR, Workstream 2, SSE NINES
Smart Solution Relevance (WS3 Ph1) | Smart Solution Set: | Smart D-Networks 3
| Focus: | Plant & Systems reliability, failure mode detection
| Subset: | Dynamic ratings for all plant types and multi element circuits

## RTTR_EHV_OHL
Solution Overview | Representative Solution: | RTTR |  |  |  | Smart Variant | discount rate | 3.5%
| Variant Solution: | RTTR for EHV OH lines |  |  |  |  | Y1 | 0 | 0 | 0 | annual opex (per feeder)
| Description: | The use of measurement and ambient forecasting data to predict the rating (and hence current carrying capacity) of assets in a real-time mode. This variant considers RTTR for EHV overhead line circuits. |  |  |  |  | y2 | 500 | 0 | 0
|  | EHV | HV | LV | Comments |  | Y3 | 500 | 0 | 0
Headroom Release (%) | Thermal Cable: | 25% | !% | !% | The headroom for RTTR OHL is extremely site specific and the benefits notes are indicative only. Any implementation will need a full site survey to identify real benefits. Furthermore it is likely to be available linked only to new generation connections or DSR. Much further work is required to identify how frequently RTTR OHL can actually be deployed on a network. Furthermore, full deployment of RTTR OHL may not be available until a full review of current ESQCR regulations are conducted. For these reasons we do not expect wide scale deployment of RTTR OHL in the next few years. |  | Y4 | 500 | 0 | 0
| Thermal Transformer: | 0% | !% | !% | No benefit expected |  | Y5 | 500 | 0 | 0
| Voltage Head: | 0% | !% | !% | No benefit expected |  | Y6 | 500 | 0 | 0
| Voltage Leg: | 0% | !% | !% | No benefit expected |  | Y7 | 500 | 0 | 0
| Power Quality: | 0% | !% | !% | No benefit expected |  | Y8 | 500 | 0 | 0
| Fault Level: | 0% | !% | !% | No benefit expected |  | Y9 | 500 | 0 | 0
Cost (£) | Capital: | 16600 |  |  | Estimate based on the purchase and installation of monitoring devices (e.g. conductor mounted measurement devices) at key points along the overhead line circuit. |  | Y10 | 500 | 0 | 0
| Operational Expenditure: | 0 |  |  | No ongoing opex cost assumed (NB. Costs of weather monitoring are factored into the associated Enabler) |  | Y11 | 500 | 0 | 0
| NPV of Opex: | 0 |  |  | Based on 20 year of annual operating expenditure @ 3.5% discount rate |  | Y12 | 500 | 0 | 0
| Cost Curve Type: | 3 |  |  | Assume a reduction in costs as solution volumes increase |  | Y13 | 500 | 0 | 0
| Life Expectancy of Solution: | 15 |  |  | At present, asset life is something of an unknown. The equipment is designed to act in a “fit and forget” manner without the requirement for ongoing maintenance. The life of the equipment for overhead line dynamic thermal ratings solutions (i.e. “power donuts”, current transformers etc.) is assumed to be 15 years; |  | Y14 | 500 | 0 | 0
| Totex (£): | 16600 |  |  | Calculated from capex plus NPV of opex |  | Y15 | 500 | 0 | 0
Merit Order | Disuption Factor (1-5): | 2 |  |  | Low disruption as the devices can be connected to the network with minimal of impact / outages |  | Y16 | 500 | 0 | 0
| Disruption Cost (£): | 2500 |  |  | Figure based on Disruption Factor (taken from Table 13.7 in the WS3 Report) |  | Y17 | 500 | 0 | 0
| Flexibility (1-5): | 4 |  |  | Devices could easily be moved from one circuit to another within their life expectancy |  | Y18 | 500 | 0 | 0
| Lead Time | 6 |  |  | Typically 6 months lead time for acquisition
| Cross Network Benefits Factor: | 0 |  |  | No benefit expected |  | Y19 | 500 | 0 | 0
Other Benefits | Impact on Fixed Losses (%): | 0% |  |  | No benefit expected |  | Y20 | 500 | 0 | 0
| Impact on Variable Losses (%): | 20% |  |  | Solution is expected to increase the variable losses (I²R) as more current is pushed down the circuit. The exact increase depends on the magnitude and duration of operating at these higher currents.
| Impact on quality of Supply (%): | 1% |  |  | A marginal benefit to QoS as this solution may provide additional monitoring of the network, potentially assisting DNOs in identifying faults or fault locations.
Year solution is available: |  | 2015 |  |  | Estimate - based on CLNR field trial
Year data (on soln) is available: |  | 2015 |  |  | Estimate - based on CLNR field trial
Source of Data: |  | CLNR, Workstream 2, WPD 132kV, SP Dynamic Rating
Smart Solution Relevance (WS3 Ph1) | Smart Solution Set: | Smart D-Networks 3
| Focus: | Plant & Systems reliability, failure mode detection
| Subset: | Dynamic ratings for all plant types and multi element circuits

## RTTR_HV_OHL
Solution Overview | Representative Solution: | RTTR |  |  |  | Smart Variant | discount rate | 3.5%
| Variant Solution: | RTTR for HV OH lines |  |  |  |  | Y1 | #REF! | 0 | 0 | annual opex (per feeder)
| Description: | The use of measurement and ambient forecasting data to predict the rating (and hence current carrying capacity) of assets in a real-time mode. This variant considers RTTR for HV overhead line circuits. |  |  |  |  | y2 | 500 | 0 | 0
|  | EHV | HV | LV | Comments |  | Y3 | 500 | 0 | 0
Headroom Release (%) | Thermal Cable: | !% | 14% | !% | The headroom for RTTR OHL is extremely site specific and the benefits notes are indicative only. Any implementation will need a full site survey to identify real benefits. Furthermore it is likely to be available linked only to new generation connections or DSR. Much further work is required to identify how frequently RTTR OHL can actually be deployed on a network. Furthermore, full deployment of RTTR OHL may not be available until a full review of current ESQCR regulations are conducted. For these reasons we do not expect wide scale deployment of RTTR OHL in the next few years. |  | Y4 | 500 | 0 | 0
| Thermal Transformer: | !% | 0% | !% | No benefit expected |  | Y5 | 500 | 0 | 0
| Voltage Head: | !% | 0% | !% | No benefit expected |  | Y6 | 500 | 0 | 0
| Voltage Leg: | !% | 0% | !% | No benefit expected |  | Y7 | 500 | 0 | 0
| Power Quality: | !% | 0% | !% | No benefit expected |  | Y8 | 500 | 0 | 0
| Fault Level: | !% | 0% | !% | No benefit expected |  | Y9 | 500 | 0 | 0
Cost (£) | Capital: | 12300 |  |  | Estimate based on the purchase and installation of monitoring devices (e.g. conductor mounted measurement devices) at key points along the overhead line circuit. |  | Y10 | 500 | 0 | 0
| Operational Expenditure: | 0 |  |  | No ongoing opex cost assumed (NB. Costs of weather monitoring are factored into the associated Enabler) |  | Y11 | 500 | 0 | 0
| NPV of Opex: | 0 |  |  | Based on 20 year of annual operating expenditure @ 3.5% discount rate |  | Y12 | 500 | 0 | 0
| Cost Curve Type: | 3 |  |  | Assume a reduction in costs as solution volumes increase |  | Y13 | 500 | 0 | 0
| Life Expectancy of Solution: | 15 |  |  | At present, asset life is something of an unknown. The equipment is designed to act in a “fit and forget” manner without the requirement for ongoing maintenance. The life of the equipment for overhead line dynamic thermal ratings solutions (i.e. “power donuts”, current transformers etc.) is assumed to be 15 years; |  | Y14 | 500 | 0 | 0
| Totex (£): | 12300 |  |  | Calculated from capex plus NPV of opex |  | Y15 | 500 | 0 | 0
Merit Order | Disuption Factor (1-5): | 2 |  |  | Low disruption as the devices can be connected to the network with minimal of impact / outages |  | Y16 | 500 | 0 | 0
| Disruption Cost (£): | 2500 |  |  | Figure based on Disruption Factor (taken from Table 13.7 in the WS3 Report) |  | Y17 | 500 | 0 | 0
| Flexibility (1-5): | 4 |  |  | Devices could easily be moved from one circuit to another within their life expectancy |  | Y18 | 500 | 0 | 0
| Lead Time | 6 |  |  | Typically 6 months lead time for acquisition
| Cross Network Benefits Factor: | 0 |  |  | No benefit expected |  | Y19 | 500 | 0 | 0
Other Benefits | Impact on Fixed Losses (%): | 0% |  |  | No benefit expected |  | Y20 | 500 | 0 | 0
| Impact on Variable Losses (%): | 20% |  |  | Solution is expected to increase the variable losses (I²R) as more current is pushed down the circuit. The exact increase depends on the magnitude and duration of operating at these higher currents.
| Impact on quality of Supply (%): | 0.01% |  |  | A marginal benefit to QoS as this solution may provide additional monitoring of the network, potentially assisting DNOs in identifying faults or fault locations.
Year solution is available: |  | 2015 |  |  | Based on CLNR
Year data (on soln) is available: |  | 2015 |  |  | Based on CLNR
Source of Data: |  | CLNR, SSE T1 33kV, Workstream 2, SP Flexible Networks, SSE NINES, UKPN Flexible plug and play
Smart Solution Relevance (WS3 Ph1) | Smart Solution Set: | Smart D-Networks 3
| Focus: | Plant & Systems reliability, failure mode detection
| Subset: | Dynamic ratings for all plant types and multi element circuits

## RTTR_EHV_Tx
Solution Overview | Representative Solution: | RTTR |  |  |  | Smart Variant | discount rate | 3.5%
| Variant Solution: | RTTR for EHV/HV Tx |  |  |  |  | Y1 | 0 | 0 | 0 | annual opex (per feeder)
| Description: | The use of measurement and ambient forecasting data to predict the rating (and hence current carrying capacity) of assets in a real-time mode. This variant considers RTTR for Primary transformers. |  |  |  |  | y2 | 500 | 0 | 0
|  | EHV | HV | LV | Comments |  | Y3 | 500 | 0 | 0
Headroom Release (%) | Thermal Cable: | 0% | !% | !% | No benefit |  | Y4 | 500 | 0 | 0
| Thermal Transformer: | 7% | !% | !% | The amount of headroom released has been calculated from observed data in CLNR, the benefits observed are 22% against static rating which equates to around 7% benefit against cyclic rating, therefore the figure 7% headroom is used. |  | Y5 | 500 | 0 | 0
| Voltage Head: | 0% | !% | !% | No expected benefit |  | Y6 | 500 | 0 | 0
| Voltage Leg: | 0% | !% | !% | No expected benefit |  | Y7 | 500 | 0 | 0
| Power Quality: | ! | !% | !% | No expected benefit |  | Y8 | 500 | 0 | 0
| Fault Level: | ! | !% | !% | No expected benefit |  | Y9 | 500 | 0 | 0
Cost (£) | Capital: | 5000 |  |  | Estimate based on the purchase and installation of monitoring devices at a single Grid transformer. It is noted that this cost looks low, and would value more detailed assessment as trials take place. It should also be noted that the cost is shared between the average number of feeders supplied. |  | Y10 | 500 | 0 | 0
| Operational Expenditure: | 0 |  |  | No ongoing opex cost assumed (NB. Costs of weather monitoring are factored into the associated Enabler) |  | Y11 | 500 | 0 | 0
| NPV of Opex: | 0 |  |  | Based on 20 year of annual operating expenditure @ 3.5% discount rate |  | Y12 | 500 | 0 | 0
| Cost Curve Type: | 3 |  |  | Assume a reduction in costs as solution volumes increase |  | Y13 | 500 | 0 | 0
| Life Expectancy of Solution: | 40 |  |  | At present, asset life is something of an unknown. The equipment is designed to act in a “fit and forget” manner without the requirement for ongoing maintenance. The life of the equipment for transformer thermal ratings solutions is assumed to align with the transformer itself (c40yrs) |  | Y14 | 500 | 0 | 0
| Totex (£): | 12281 |  |  | Calculated from capex plus NPV of opex |  | Y15 | 500 | 0 | 0
Merit Order | Disuption Factor (1-5): | 2 |  |  | Low disruption as the devices can be connected to the network with minimal of impact / outages |  | Y16 | 500 | 0 | 0
| Disruption Cost (£): | 2500 |  |  | Figure based on Disruption Factor (taken from Table 13.7 in the WS3 Report) |  | Y17 | 500 | 0 | 0
| Flexibility (1-5): | 4 |  |  | Devices could easily be moved from one circuit to another within their life expectancy |  | Y18 | 500 | 0 | 0
| Lead Time | 6 |  |  | Typically 6 months lead time for acquisition
| Cross Network Benefits Factor: | 0 |  |  | No benefit expected |  | Y19 | 500 | 0 | 0
Other Benefits | Impact on Fixed Losses (%): | 0% |  |  | No benefit expected |  | Y20 | 500 | 0 | 0
| Impact on Variable Losses (%): | 20% |  |  | Solution is expected to increase the variable losses (I²R) as more current is pushed down the circuit. The exact increase depends on the magnitude and duration of operating at these higher currents.
| Impact on quality of Supply (%): | 0% |  |  | No benefit expected
Year solution is available: |  | 2015 |  |  | Based on CLNR
Year data (on soln) is available: |  | 2015 |  |  | Based on CLNR
Source of Data: |  | CLNR, Workstream 2, SP Flexible Networks
Smart Solution Relevance (WS3 Ph1) | Smart Solution Set: | Smart D-Networks 3
| Focus: | Plant & Systems reliability, failure mode detection
| Subset: | Dynamic ratings for all plant types and multi element circuits

## RTTR_HV_Tx
Solution Overview | Representative Solution: | RTTR |  |  |  | Smart Variant | discount rate | 3.5%
| Variant Solution: | RTTR for HV/LV Tx |  |  |  |  | Y1 | #REF! | 0 | 0 | annual opex (per feeder)
| Description: | The use of measurement and ambient forecasting data to predict the rating (and hence current carrying capacity) of assets in a real-time mode. This variant considers RTTR for Secondary distribution transformers. |  |  |  |  | y2 | 500 | 0 | 0
|  | EHV | HV | LV | Comments |  | Y3 | 500 | 0 | 0
Headroom Release (%) | Thermal Cable: | !% | !% | 0% | No benefit |  | Y4 | 500 | 0 | 0
| Thermal Transformer: | !% | !% | 15% | The amount of headroom released has been calculated from observed data in CLNR, the benefits observed are 30% against static rating which equates to around 15% benefit against cyclic rating, therefore the figure 7% headroom is used. |  | Y5 | 500 | 0 | 0
| Voltage Head: | !% | !% | 0% | No expected benefit |  | Y6 | 500 | 0 | 0
| Voltage Leg: | !% | !% | 0% | No expected benefit |  | Y7 | 500 | 0 | 0
| Power Quality: | !% | !% | 0% | No expected benefit |  | Y8 | 500 | 0 | 0
| Fault Level: | !% | !% | 0% | No expected benefit |  | Y9 | 500 | 0 | 0
Cost (£) | Capital: | 1457 |  |  | Estimate based on the purchase and installation of monitoring devices at a single Grid transformer. |  | Y10 | 500 | 0 | 0
| Operational Expenditure: | 0 |  |  | No ongoing opex cost assumed (NB. Costs of weather monitoring are factored into the associated Enabler) |  | Y11 | 500 | 0 | 0
| NPV of Opex: | 0 |  |  | Based on 20 year of annual operating expenditure @ 3.5% discount rate |  | Y12 | 500 | 0 | 0
| Cost Curve Type: | 3 |  |  | Assume a reduction in costs as solution volumes increase |  | Y13 | 500 | 0 | 0
| Life Expectancy of Solution: | 20 |  |  | At present, asset life is something of an unknown. The equipment is designed to act in a “fit and forget” manner without the requirement for ongoing maintenance. The life of the equipment for transformer thermal ratings solutions is assumed to align with the transformer itself (c40yrs) |  | Y14 | 500 | 0 | 0
| Totex (£): | 1457 |  |  | Calculated from capex plus NPV of opex |  | Y15 | 500 | 0 | 0
Merit Order | Disuption Factor (1-5): | 2 |  |  | Low disruption as the devices can be connected to the network with minimal of impact / outages |  | Y16 | 500 | 0 | 0
| Disruption Cost (£): | 2500 |  |  | Figure based on Disruption Factor (taken from Table 13.7 in the WS3 Report) |  | Y17 | 500 | 0 | 0
| Flexibility (1-5): | 4 |  |  | Devices could easily be moved from one circuit to another within their life expectancy |  | Y18 | 500 | 0 | 0
| Lead Time | 6 |  |  | Typically 6 months lead time for acquisition
| Cross Network Benefits Factor: | 0 |  |  | No benefit expected |  | Y19 | 500 | 0 | 0
Other Benefits | Impact on Fixed Losses (%): | 0% |  |  | No benefit expected |  | Y20 | 500 | 0 | 0
| Impact on Variable Losses (%): | 10% |  |  | Solution is expected to increase the variable losses (I²R) as more current is pushed down the circuit. The exact increase depends on the magnitude and duration of operating at these higher currents.
| Impact on quality of Supply (%): | 1% |  |  | No benefit expected
Year solution is available: |  | 2015 |  |  | Estimate - based on transformer RTTR being an incremental development
Year data (on soln) is available: |  | 2013 |  |  | Expect futher data from trials such as CLNR as the project completes (Dec 2013)
Source of Data: |  | CLNR, Workstream 2
Smart Solution Relevance (WS3 Ph1) | Smart Solution Set: | Smart D-Networks 3
| Focus: | Plant & Systems reliability, failure mode detection
| Subset: | Dynamic ratings for all plant types and multi element circuits

## EAVC_HV
Solution Overview | Representative Solution: | Enhanced Automatic voltage Control (EAVC) |  |  |  | Smart Variant | discount rate | 3.5%
| Variant Solution: | HV circuit voltage regulators |  |  |  |  | Y1 | #REF! | 0 | 0 | annual opex (per feeder)
| Description: | As tested on CLNR, the regulators only boost. They do not buck. However, other regulators could be fitted which do boost and buck. This would change the benefit to 5% headroom and 5% legroom |  |  |  |  | y2 | 500 | 0 | 0
|  | EHV | HV | LV | Comments |  | Y3 | 500 | 0 | 0
Headroom Release (%) | Thermal Cable: | !% | 0% | !% | No expected benefit |  | Y4 | 500 | 0 | 0
| Thermal Transformer: | !% | 0% | !% | No expected benefit |  | Y5 | 500 | 0 | 0
| Voltage Head: | !% | 0% | !% | Could be used to resolve high volts issues for a number of customers |  | Y6 | 500 | 0 | 0
| Voltage Leg: | !% | 9.8% | !% | Could be used to resolve low volts issues for a number of customers |  | Y7 | 500 | 0 | 0
| Power Quality: | !% | 0% | !% | No expected benefit |  | Y8 | 500 | 0 | 0
| Fault Level: | !% | 0% | !% | No expected benefit |  | Y9 | 500 | 0 | 0
Cost (£) | Capital: | 52000 |  |  | Estimated cost for purchase and installation (per feeder) |  | Y10 | 500 | 0 | 0
| Operational Expenditure: | 0 |  |  | Assumed to be “fit and forget” maintenance-free devices - therefore no ongoing operational expenditure assumed for this solution. |  | Y11 | 500 | 0 | 0
| NPV of Opex: | 0 |  |  | Based on 20 year of annual operating expenditure @ 3.5% discount rate |  | Y12 | 500 | 0 | 0
| Cost Curve Type: | 2 |  |  | LV application could see such a unit becoming relatively high volume, with sharp roll-off rates |  | Y13 | 500 | 0 | 0
| Life Expectancy of Solution: | 20 |  |  | Estimated life expectancy of this type of equipment |  | Y14 | 500 | 0 | 0
| Totex (£): | 52000 |  |  | Calculated from capex plus NPV of opex |  | Y15 | 500 | 0 | 0
Merit Order | Disuption Factor (1-5): | 2 |  |  | Likely to disrupt a number of customers down an LV feeder at time of installation/commissioning |  | Y16 | 500 | 0 | 0
| Disruption Cost (£): | 2500 |  |  | Figure based on Disruption Factor (taken from Table 13.7 in the WS3 Report) |  | Y17 | 500 | 0 | 0
| Flexibility (1-5): | 4 |  |  | These products could be easily redeployed as other (more widespread) solutions are used |  | Y18 | 500 | 0 | 0
| Lead Time | 6 |  |  | Typically 6 months lead time for acquisition
| Cross Network Benefits Factor: | 1 |  |  | Potential to allow HV volts to operate outside of statutory limits (whilst ensuring LV customers receive volts within limits) |  | Y19 | 500 | 0 | 0
Other Benefits | Impact on Fixed Losses (%): | 2% |  |  | Lossy devices, expected to give rise to a small increase in losses |  | Y20 | 500 | 0 | 0
| Impact on Variable Losses (%): | 0% |  |  | No change to variable losses anticipated with this solution
| Impact on quality of Supply (%): | 0% |  |  | No expected benefit
Year solution is available: |  | 2012 |  |  | Solutions are in use today, but not at scale
Year data (on soln) is available: |  | 2013 |  |  | CLNR
Source of Data: |  | CLNR
Smart Solution Relevance (WS3 Ph1) | Smart Solution Set: | Smart D-Networks 2
| Focus: | DG connections, management of two way power flows
| Subset: | Intelligent voltage control

## EAVC_LV
Solution Overview | Representative Solution: | Enhanced Automatic voltage Control (EAVC) |  |  |  | Smart Variant | discount rate | 3.5%
| Variant Solution: | LV circuit voltage regulators |  |  |  |  | Y1 | #REF! | 0 | 0 | annual opex (per feeder)
| Description: | As tested on CLNR, no improved benefit observed for operation of GUS. A much greater benefit could be obtained with a wider tapping range available. This was due to lack of availability at the time of installation. |  |  |  |  | y2 | 500 | 0 | 0
|  | EHV | HV | LV | Comments |  | Y3 | 500 | 0 | 0
Headroom Release (%) | Thermal Cable: | !% | !% | 0% | No expected benefit |  | Y4 | 500 | 0 | 0
| Thermal Transformer: | !% | !% | 0% | No expected benefit |  | Y5 | 500 | 0 | 0
| Voltage Head: | !% | !% | 1.25% | Could be used to resolve high volts issues for a number of customers |  | Y6 | 500 | 0 | 0
| Voltage Leg: | !% | !% | 1.25% | Could be used to resolve low volts issues for a number of customers |  | Y7 | 500 | 0 | 0
| Power Quality: | !% | !% | 0% | No expected benefit |  | Y8 | 500 | 0 | 0
| Fault Level: | !% | !% | 0% | No expected benefit |  | Y9 | 500 | 0 | 0
Cost (£) | Capital: | 100000 |  |  | Estimated cost for purchase and installation (per feeder) |  | Y10 | 500 | 0 | 0
| Operational Expenditure: | 0 |  |  | Assumed to be “fit and forget” maintenance-free devices - therefore no ongoing operational expenditure assumed for this solution. |  | Y11 | 500 | 0 | 0
| NPV of Opex: | 0 |  |  | Based on 20 year of annual operating expenditure @ 3.5% discount rate |  | Y12 | 500 | 0 | 0
| Cost Curve Type: | 2 |  |  | LV application could see such a unit becoming relatively high volume, with sharp roll-off rates |  | Y13 | 500 | 0 | 0
| Life Expectancy of Solution: | 20 |  |  | Estimated life expectancy of this type of equipment |  | Y14 | 500 | 0 | 0
| Totex (£): | 93000 |  |  | Calculated from capex plus NPV of opex |  | Y15 | 500 | 0 | 0
Merit Order | Disuption Factor (1-5): | 2 |  |  | Likely to disrupt a number of customers down an LV feeder at time of installation/commissioning |  | Y16 | 500 | 0 | 0
| Disruption Cost (£): | 2500 |  |  | Figure based on Disruption Factor (taken from Table 13.7 in the WS3 Report) |  | Y17 | 500 | 0 | 0
| Flexibility (1-5): | 4 |  |  | These products could be easily redeployed as other (more widespread) solutions are used |  | Y18 | 500 | 0 | 0
| Lead Time | 6 |  |  | Typically 6 months lead time for acquisition
| Cross Network Benefits Factor: | 1 |  |  | Potential to allow HV volts to operate outside of statutory limits (whilst ensuring LV customers receive volts within limits) |  | Y19 | 500 | 0 | 0
Other Benefits | Impact on Fixed Losses (%): | 2% |  |  | Lossy devices, expected to give rise to a small increase in losses |  | Y20 | 500 | 0 | 0
| Impact on Variable Losses (%): | 0% |  |  | No change to variable losses anticipated with this solution
| Impact on quality of Supply (%): | 0% |  |  | No expected benefit
Year solution is available: |  | 2012 |  |  | Solutions are in use today, but not at scale
Year data (on soln) is available: |  | 2013 |  |  | well proven
Source of Data: |  | CLNR
Smart Solution Relevance (WS3 Ph1) | Smart Solution Set: | Smart D-Networks 2
| Focus: | DG connections, management of two way power flows
| Subset: | Intelligent voltage control

## EAVC_HV_LV_Tx
Solution Overview | Representative Solution: | Enhanced Automatic voltage Control (EAVC) |  |  |  | Smart Variant | discount rate | 3.5%
| Variant Solution: | HV/LV Transformer Voltage Control |  |  |  |  | Y1 | #REF! | 0 | 0 | annual opex (per feeder)
| Description: | CLNR tested 3 of these devices, there are now around 1200 on networks around the world and these are well proven devices. |  |  |  |  | y2 | 500 | 0 | 0
|  | EHV | HV | LV | Comments |  | Y3 | 500 | 0 | 0
Headroom Release (%) | Thermal Cable: | !% | !% | 0% | No expected benefit |  | Y4 | 500 | 0 | 0
| Thermal Transformer: | !% | !% | 0% | No expected benefit |  | Y5 | 500 | 0 | 0
| Voltage Head: | !% | !% | 8.7% | Could be used to resolve high volts issues for a number of customers, based on CLNR data |  | Y6 | 500 | 0 | 0
| Voltage Leg: | !% | !% | 7.4% | Could be used to resolve high volts issues for a number of customers, based on CLNR data |  | Y7 | 500 | 0 | 0
| Power Quality: | !% | !% | 0% | No expected benefit |  | Y8 | 500 | 0 | 0
| Fault Level: | !% | !% | 0% | No expected benefit |  | Y9 | 500 | 0 | 0
Cost (£) | Capital: | 9026 |  |  | Based on CLNR data |  | Y10 | 500 | 0 | 0
| Operational Expenditure: | 0 |  |  | Assumed maintenance costs |  | Y11 | 500 | 0 | 0
| NPV of Opex: | 0 |  |  | Based on 20 year of annual operating expenditure @ 3.5% discount rate |  | Y12 | 500 | 0 | 0
| Cost Curve Type: | 3 |  |  | Now widely available and costs likely to reduce (from CLNR) |  | Y13 | 500 | 0 | 0
| Life Expectancy of Solution: | 40 |  |  | Estimated life expectancy of a distribution transformer |  | Y14 | 500 | 0 | 0
| Totex (£): | 9026 |  |  | Calculated from capex plus NPV of opex |  | Y15 | 500 | 0 | 0
Merit Order | Disuption Factor (1-5): | 3 |  |  | Likely to disrupt a number of customers down an LV feeder at time of installation/commissioning |  | Y16 | 500 | 0 | 0
| Disruption Cost (£): | 10000 |  |  | Figure based on Disruption Factor (taken from Table 13.7 in the WS3 Report) |  | Y17 | 500 | 0 | 0
| Flexibility (1-5): | 2 |  |  | Unlikely to be redeployed after initial installation |  | Y18 | 500 | 0 | 0
| Lead Time | 6 |  |  | Typically 6 months lead time for acquisition
| Cross Network Benefits Factor: | 1 |  |  | Potential to allow HV volts to operate outside of statutory limits (whilst ensuring LV customers receive volts within limits) |  | Y19 | 500 | 0 | 0
Other Benefits | Impact on Fixed Losses (%): | 2% |  |  | Lossy devices, expected to give rise to a small increase in losses, not measured in CLNR - difficult to estimate. |  | Y20 | 500 | 0 | 0
| Impact on Variable Losses (%): | 0% |  |  | No change to variable losses anticipated with this solution
| Impact on quality of Supply (%): | 0% |  |  | No expected benefit
Year solution is available: |  | 2015 |  |  | Based on CLNR data
Year data (on soln) is available: |  | 2015 |  |  | Based on CLNR data
Source of Data: |  | CLNR
Smart Solution Relevance (WS3 Ph1) | Smart Solution Set: | CLNR
| Focus: | DG connections, management of two way power flows
| Subset: | Intelligent voltage control

## Switched Capacitors
Solution Overview | Representative Solution: | Enhanced Automatic voltage Control (EAVC) |  |  |  | SMART VARIANT | discount rate | 3.5%
| Variant Solution: | Switched Capacitors |  |  |  |  | Y1 | #REF! | #REF! | #REF! | annual opex (per feeder)
| Description: | As trialled in CLNR. |  |  |  |  | y2 | 500 | #REF! | #REF!
|  | EHV | HV | LV | Comments |  | Y3 | 500 | #REF! | #REF!
Headroom Release (%) | Thermal Cable: | !% | 0% | !% | No expected benefit |  | Y4 | 500 | #REF! | #REF!
| Thermal Transformer: | !% | 0% | !% | No expected benefit |  | Y5 | 500 | #REF! | #REF!
| Voltage Head: | !% | 0% | !% | Could be used to resolve high volts issues for a number of customers, but not in the CLNR configuration. |  | Y6 | 500 | #REF! | #REF!
| Voltage Leg: | !% | 11.6% | !% | Could be used to resolve low volts issues for a number of customers |  | Y7 | 500 | #REF! | #REF!
| Power Quality: | !% | 0% | !% | No expected benefit |  | Y8 | 500 | #REF! | #REF!
| Fault Level: | !% | 0% | !% | No expected benefit |  | Y9 | 500 | #REF! | #REF!
Cost (£) | Capital: | 2000000 |  |  | Estimated cost for purchase and installation (per feeder) |  | Y10 | 500 | #REF! | #REF!
| Operational Expenditure: | 0 |  |  | Assumed to be “fit and forget” maintenance-free devices - therefore no ongoing operational expenditure assumed for this solution. |  | Y11 | 500 | #REF! | #REF!
| NPV of Opex: | 0 |  |  | Based on 20 year of annual operating expenditure @ 3.5% discount rate |  | Y12 | 500 | #REF! | #REF!
| Cost Curve Type: | 2 |  |  | LV application could see such a unit becoming relatively high volume, with sharp roll-off rates |  | Y13 | 500 | #REF! | #REF!
| Life Expectancy of Solution: | 20 |  |  | Estimated life expectancy of this type of equipment |  | Y14 | 500 | #REF! | #REF!
| Totex (£): | 2000000 |  |  | Calculated from capex plus NPV of opex |  | Y15 | 500 | #REF! | #REF!
Merit Order | Disuption Factor (1-5): | 2 |  |  | Likely to disrupt a number of customers down an LV feeder at time of installation/commissioning |  | Y16 | 500 | #REF! | #REF!
| Disruption Cost (£): | 2500 |  |  | Figure based on Disruption Factor (taken from Table 13.7 in the WS3 Report) |  | Y17 | 500 | #REF! | #REF!
| Flexibility (1-5): | 4 |  |  | These products could be easily redeployed as other (more widespread) solutions are used |  | Y18 | 500 | #REF! | #REF!
| Lead Time | 6 |  |  | Typically 6 months lead time for acquisition
| Cross Network Benefits Factor: | 1 |  |  | Potential to allow HV volts to operate outside of statutory limits (whilst ensuring LV customers receive volts within limits) |  | Y19 | 500 | #REF! | #REF!
Other Benefits | Impact on Fixed Losses (%): | 2% |  |  | Lossy devices, expected to give rise to a small increase in losses |  | Y20 | 500 | #REF! | #REF!
| Impact on Variable Losses (%): | 0% |  |  | No change to variable losses anticipated with this solution
| Impact on quality of Supply (%): | 0% |  |  | No expected benefit
Year solution is available: |  | 2012 |  |  | Solutions are in use today, but not at scale
Year data (on soln) is available: |  | 2013 |  |  | CLNR
Source of Data: |  | CLNR
Smart Solution Relevance (WS3 Ph1) | Smart Solution Set: | Smart D-Networks 2
| Focus: | DG connections, management of two way power flows
| Subset: | Intelligent voltage control

## EAVC_HV_LV_Tx_GUS
Solution Overview | Representative Solution: | Enhanced Automatic voltage Control (EAVC) |  |  |  | SMART VARIANT | discount rate | 3.5%
| Variant Solution: | HV/LV Transformer Voltage Control with GUS |  |  |  |  | Y1 | #REF! | #REF! | #REF! | annual opex (per feeder)
| Description: | CLNR tested 3 of these devices, there are now around 1200 on networks around the world and these are well proven devices. Using GUS can provide the full 16% of headroom and or legroon rather than either or. |  |  |  |  | y2 | 500 | #REF! | #REF!
|  | EHV | HV | LV | Comments |  | Y3 | 500 | #REF! | #REF!
Headroom Release (%) | Thermal Cable: | !% | !% | 0% | No expected benefit |  | Y4 | 500 | #REF! | #REF!
| Thermal Transformer: | !% | !% | 0% | No expected benefit |  | Y5 | 500 | #REF! | #REF!
| Voltage Head: | !% | !% | 16% | Could be used to resolve high volts issues for a number of customers, based on CLNR data |  | Y6 | 500 | #REF! | #REF!
| Voltage Leg: | !% | !% | 16% | Could be used to resolve high volts issues for a number of customers, based on CLNR data |  | Y7 | 500 | #REF! | #REF!
| Power Quality: | !% | !% | 0% | No expected benefit |  | Y8 | 500 | #REF! | #REF!
| Fault Level: | !% | !% | 0% | No expected benefit |  | Y9 | 500 | #REF! | #REF!
Cost (£) | Capital: | 9026 |  |  | Based on CLNR data |  | Y10 | 500 | #REF! | #REF!
| Operational Expenditure: | 0 |  |  |  |  | Y11 | 500 | #REF! | #REF!
| NPV of Opex: | 0 |  |  | Based on 20 year of annual operating expenditure @ 3.5% discount rate |  | Y12 | 500 | #REF! | #REF!
| Cost Curve Type: | 3 |  |  | Now widely available and costs likely to reduce (from CLNR) |  | Y13 | 500 | #REF! | #REF!
| Life Expectancy of Solution: | 40 |  |  | Estimated life expectancy of a distribution transformer |  | Y14 | 500 | #REF! | #REF!
| Totex (£): | 9026 |  |  | Calculated from capex plus NPV of opex |  | Y15 | 500 | #REF! | #REF!
Merit Order | Disuption Factor (1-5): | 3 |  |  | Likely to disrupt a number of customers down an LV feeder at time of installation/commissioning |  | Y16 | 500 | #REF! | #REF!
| Disruption Cost (£): | 10000 |  |  | Figure based on Disruption Factor (taken from Table 13.7 in the WS3 Report) |  | Y17 | 500 | #REF! | #REF!
| Flexibility (1-5): | 2 |  |  | Unlikely to be redeployed after initial installation |  | Y18 | 500 | #REF! | #REF!
| Lead Time | 6 |  |  | Typically 6 months lead time for acquisition
| Cross Network Benefits Factor: | 1 |  |  | Potential to allow HV volts to operate outside of statutory limits (whilst ensuring LV customers receive volts within limits) |  | Y19 | 500 | #REF! | #REF!
Other Benefits | Impact on Fixed Losses (%): | 2% |  |  | Lossy devices, expected to give rise to a small increase in losses |  | Y20 | 500 | #REF! | #REF!
| Impact on Variable Losses (%): | 0% |  |  | No change to variable losses anticipated with this solution
| Impact on quality of Supply (%): | 0% |  |  | No expected benefit
Year solution is available: |  | 2015 |  |  | Based on CLNR data
Year data (on soln) is available: |  | 2015 |  |  | Based on CLNR data
Source of Data: |  | CLNR
Smart Solution Relevance (WS3 Ph1) | Smart Solution Set: | CLNR
| Focus: | DG connections, management of two way power flows
| Subset: | Intelligent voltage control

## EAVC_LV_NXTGEN
Solution Overview | Representative Solution: | Enhanced Automatic voltage Control (EAVC) |  |  |  | SMART VARIANT | discount rate | 3.5%
| Variant Solution: | LV circuit voltage regulators |  |  |  |  | Y1 | #REF! | #REF! | #REF! | annual opex (per feeder)
| Description: | As tested on CLNR, no improved benefit observed for operation of GUS. A much greater benefit could be obtained with a wider tapping range available which we assume can be available in 2 years. |  |  |  |  | y2 | 500 | #REF! | #REF!
|  | EHV | HV | LV | Comments |  | Y3 | 500 | #REF! | #REF!
Headroom Release (%) | Thermal Cable: | !% | !% | 0% | No expected benefit |  | Y4 | 500 | #REF! | #REF!
| Thermal Transformer: | !% | !% | 0% | No expected benefit |  | Y5 | 500 | #REF! | #REF!
| Voltage Head: | !% | !% | 5% | Could be used to resolve high volts issues for a number of customers |  | Y6 | 500 | #REF! | #REF!
| Voltage Leg: | !% | !% | 5% | Could be used to resolve low volts issues for a number of customers |  | Y7 | 500 | #REF! | #REF!
| Power Quality: | !% | !% | 0% | No expected benefit |  | Y8 | 500 | #REF! | #REF!
| Fault Level: | !% | !% | 0% | No expected benefit |  | Y9 | 500 | #REF! | #REF!
Cost (£) | Capital: | 100000 |  |  | Estimated cost for purchase and installation (per feeder) |  | Y10 | 500 | #REF! | #REF!
| Operational Expenditure: | 0 |  |  | Assumed to be “fit and forget” maintenance-free devices - therefore no ongoing operational expenditure assumed for this solution. |  | Y11 | 500 | #REF! | #REF!
| NPV of Opex: | 0 |  |  | Based on 20 year of annual operating expenditure @ 3.5% discount rate |  | Y12 | 500 | #REF! | #REF!
| Cost Curve Type: | 2 |  |  | LV application could see such a unit becoming relatively high volume, with sharp roll-off rates |  | Y13 | 500 | #REF! | #REF!
| Life Expectancy of Solution: | 20 |  |  | Estimated life expectancy of this type of equipment |  | Y14 | 500 | #REF! | #REF!
| Totex (£): | 93000 |  |  | Calculated from capex plus NPV of opex |  | Y15 | 500 | #REF! | #REF!
Merit Order | Disuption Factor (1-5): | 2 |  |  | Likely to disrupt a number of customers down an LV feeder at time of installation/commissioning |  | Y16 | 500 | #REF! | #REF!
| Disruption Cost (£): | 2500 |  |  | Figure based on Disruption Factor (taken from Table 13.7 in the WS3 Report) |  | Y17 | 500 | #REF! | #REF!
| Flexibility (1-5): | 4 |  |  | These products could be easily redeployed as other (more widespread) solutions are used |  | Y18 | 500 | #REF! | #REF!
| Lead Time | 6 |  |  | Typically 6 months lead time for acquisition
| Cross Network Benefits Factor: | 1 |  |  | Potential to allow HV volts to operate outside of statutory limits (whilst ensuring LV customers receive volts within limits) |  | Y19 | 500 | #REF! | #REF!
Other Benefits | Impact on Fixed Losses (%): | 2% |  |  | Lossy devices, expected to give rise to a small increase in losses |  | Y20 | 500 | #REF! | #REF!
| Impact on Variable Losses (%): | 0% |  |  | No change to variable losses anticipated with this solution
| Impact on quality of Supply (%): | 0% |  |  | No expected benefit
Year solution is available: |  | 2017 |  |  | waiting on better availability - ref CLNR
Year data (on soln) is available: |  | 2017 |  |  | CLNR
Source of Data: |  | CLNR
Smart Solution Relevance (WS3 Ph1) | Smart Solution Set: | Smart D-Networks 2
| Focus: | DG connections, management of two way power flows
| Subset: | Intelligent voltage control

## Storage HV EES Medium
Solution Overview | Representative Solution: | Energy Storage |  |  |  | Smart Variant | discount rate | 3.5%
| Variant Solution: | Electrical Energy Storage_HV connected EES - medium |  |  |  |  | Y1 | 18059.86 | 0 | 0 | annual opex (per feeder)
| Description: | Electrical Energy Storage (EES) technologies (medium-sized HV connected batteries) deployed on a network to either deliver the peak demand, or absorb high levels of generation at key times of the day/year. The charge cycles of EES can be tuned to local network conditions, but is ultimately a function of the capacity (MW and MWh) of the units. Storage size for this variant is 2.5MW; 5MWh. |  |  |  |  | y2 | 18059.86 | 0 | 0
|  | EHV | HV | LV | Comments |  | Y3 | 18059.86 | 0 | 0
Headroom Release (%) | Thermal Cable: |  | 0% | !% | Determined in the Model (DM): In a similar vein to Residential DSR, this EES solution is deployed in a comprehensive 'bottom-up' manner, taking into account the magnitude and duration of the peak, and the capacity (MW and MWh) available of the storage unit. |  | Y4 | 18059.86 | 0 | 0
| Thermal Transformer: |  | 0% | !% | As Thermal Cable, this is calcuated within the model, and based on the aggregated ouput of the types of loads that can be moved. |  | Y5 | 18059.86 | 0 | 0
| Voltage Head: |  | 0% | !% | EES would typically be used to flatten peaks created by generation (e.g. high volts resulting from PV in the middle of the day or onshore windfarms under windy conditions) or load (e.g. low volts resulting from EVs at the early evening peak). |  | Y6 | 18059.86 | 0 | 0
| Voltage Leg: |  | 0% | !% | Based on the thermal profiles calculated within the model - flattening of peak demand will reduce volt drops along the circuit, thereby improving voltage legroom. |  | Y7 | 18059.86 | 0 | 0
| Power Quality: |  | 0% | !% | No modelled benefit (it is noted that the converter on the battery unit may provide some power quality support, but as the model has not been setup to consider PQ issues, analysis has not been carried out on this aspect of EES) |  | Y8 | 18059.86 | 0 | 0
| Fault Level: |  | -8% | !% | EES can be made to 'look' like a generator to the network, feeding in fault current at the time of fault. As the storage unit sits behind power electronics, this effect is damped, but as this unit is medium sized it has been modelled as reducing FL headroom by 8%. |  | Y9 | 18059.86 | 0 | 0
Cost (£) | Capital: | 999312 |  |  | Costs have been based on average prices seen in trials for the size of unit provided in 'Description' above and scaled accordingly. The costs include the procurement of storage units, power electronics, connection infrastructure, and installation & commissioning works. It should be noted that the costs are shared between the average number of feeders outgoing from the substation. |  | Y10 | 18059.86 | 0 | 0
| Operational Expenditure: | 18059.86 |  |  | Estimation of the annual cost of running communications to the devices. NB. The EES's energy costs have not been factored into this model, and are instead treated as a network loss. |  | Y11 | 18059.86 | 0 | 0
| NPV of Opex: | 333676 |  |  | Based on 20 year of annual operating expenditure @ 3.5% discount rate |  | Y12 | 18059.86 | 0 | 0
| Cost Curve Type: | 4 |  |  | In 2012, EES units are not readily available off-the-shelf, with typical lead-times of 6-18 months. This is about equivalent to the amount of time that should be allocated for pre-installation project and site preparation, fire, operation and safety procedures. HV units are unlikely to be deployed in large volumes, so whilst costs will reduce, it is not clear that they will reduce dramatically. |  | Y13 | 18059.86 | 0 | 0
| Life Expectancy of Solution: | 20 |  |  | EES asset life is electrochemically limited by the number of charge/discharge cycles that the technology can sustain without severe performance degradation. The chemicals used in flow-cell batteries are highly reactive; with every cycle the chemically active parts pollute to some degree, such that over the course of time, performance suffers. In this respect, flow cells offer the greatest potential for longevity as the active parts can be replaced or refreshed to renew performance. As life depends on cycles, limiting the number of cycles necessary to provide upgrade deferment by a form of intelligent control may be necessary. Considering daily cycles used for peak lopping over one-quarter of a year, the various technologies would have calendar lives (determined from cycle numbers per year) of up to 15 years for lead-acid and up to 30 years for sodium metal-halide. We have assumed a lifetime of 20 years within our modelling. |  | Y14 | 18059.86 | 0 | 0
| Totex (£): | 1632782 |  |  | Calculated from capex plus NPV of opex |  | Y15 | 18059.86 | 0 | 0
Merit Order | Disuption Factor (1-5): | 3 |  |  | Deployment requires suitable space to be available, which can be a premium, particularly in congested urban and suburban substations. Compared to reinforcement (e.g. the construction of new overhead lines or substations), planning processes should be reduced, although there may be additional complexities owing to the electrochemical nature of the units. |  | Y16 | 18059.86 | 0 | 0
| Disruption Cost (£): | 10000 |  |  | Figure based on Disruption Factor (taken from Table 13.7 in the WS3 Report) |  | Y17 | 18059.86 | 0 | 0
| Flexibility (1-5): | 2 |  |  | Most types of EES could be relocated or expanded in a modular manner as the need to peak lop changes over time. Given the interest in EES and the relatively limited supply capacity for utility-scale applications, availability will be subject to global markets. |  | Y18 | 18059.86 | 0 | 0
| Cross Network Benefits Factor: | 2 |  |  | Solution will provide a benefit to LV and EHV networks |  | Y19 | 18059.86 | 0 | 0
Other Benefits | Impact on Fixed Losses (%): | 20% |  |  | This solution is will increase fixed losses as the round-trip efficiency of a storage unit is less than 100% - this differs by manufacturer and storage type. |  | Y20 | 18059.86 | 0 | 0
| Impact on Variable Losses (%): | -10% |  |  | As DSR, this solution has the ability to reduce the losses down a circuit by reducing the peak demand (less current, therefore less heating loss).
| Impact on quality of Supply (%): | 0% |  |  | This solution is not expected to give any benefit to QoS
Year solution becomes available: |  | 2013 |  |  | Estimate - based on solutions being available for purchase (for trial)
Year data (on soln) is available: |  | 2013 |  |  | 0
Source of Data: |  | SGS
Smart Solution Relevance (WS3 Ph1) | Smart Solution Set: | smart
Focus:
Subset:

## Storage LV EES large
Solution Overview | Representative Solution: | Energy Storage |  |  |  | Smart Variant | discount rate | 3.5%
| Variant Solution: | Electrical Energy Storage_LV connected EES - large |  |  |  |  | Y1 | 940.26 | 0 | 0 | annual opex (per feeder)
| Description: | Electrical Energy Storage (EES) technologies (large LV connected batteries, e.g. at the distribution substation) deployed on a network to either deliver the peak demand, or absorb high levels of generation at key times of the day/year. The charge cycles of EES can be tuned to local network conditions, but is ultimately a function of the capacity (MW and MWh) of the units. Storage size for this variant is 100kW; 200kWh. |  |  |  |  | y2 | 940.26 | 0 | 0
|  | EHV | HV | LV | Comments |  | Y3 | 940.26 | 0 | 0
Headroom Release (%) | Thermal Cable: |  |  | 0% | Determined in the Model (DM): In a similar vein to Residential DSR, this EES solution is deployed in a comprehensive 'bottom-up' manner, taking into account the magnitude and duration of the peak, and the capacity (MW and MWh) available of the storage unit. |  | Y4 | 940.26 | 0 | 0
| Thermal Transformer: |  |  | 0% | As Thermal Cable, this is calcuated within the model, and based on the aggregated ouput of the types of loads that can be moved. |  | Y5 | 940.26 | 0 | 0
| Voltage Head: |  |  | 0% | EES would typically be used to flatten peaks created by generation (e.g. high volts resulting from PV in the middle of the day or onshore windfarms under windy conditions) or load (e.g. low volts resulting from EVs at the early evening peak). |  | Y6 | 940.26 | 0 | 0
| Voltage Leg: |  |  | 0% | Based on the thermal profiles calculated within the model - flattening of peak demand will reduce volt drops along the circuit, thereby improving voltage legroom. |  | Y7 | 940.26 | 0 | 0
| Power Quality: |  |  | 0% | No modelled benefit (it is noted that the converter on the battery unit may provide some power quality support, but as the model has not been setup to consider PQ issues, analysis has not been carried out on this aspect of EES) |  | Y8 | 940.26 | 0 | 0
| Fault Level: |  |  | -10% | EES can be made to 'look' like a generator to the network, feeding in fault current at the time of fault. As the storage unit sits behind power electronics, this effect is damped, but as this unit is medium sized it has been modelled as reducing FL headroom by 10%. |  | Y9 | 940.26 | 0 | 0
Cost (£) | Capital: | 46073 |  |  | Costs have been based on average prices seen in trials for the size of unit provided in 'Description' above and scaled accordingly. The costs include the procurement of storage units, power electronics, connection infrastructure, and installation & commissioning works. It should be noted that the costs are shared between the average number of feeders outgoing from the substation. |  | Y10 | 940.26 | 0 | 0
| Operational Expenditure: | 940.26 |  |  | Estimation of the annual cost of running communications to the devices. NB. The EES's energy costs have not been factored into this model, and are instead treated as a network loss. |  | Y11 | 940.26 | 0 | 0
| NPV of Opex: | 17372 |  |  | Based on 20 year of annual operating expenditure @ 3.5% discount rate |  | Y12 | 940.26 | 0 | 0
| Cost Curve Type: | 5 |  |  | In 2012, EES units are not readily available off-the-shelf, with typical lead-times of 6-18 months. This is about equivalent to the amount of time that should be allocated for pre-installation project and site preparation, fire, operation and safety procedures. LV units could be deployed in large volumes, accelerating the cost curve roll off. However, it is noted that storage is a global market and is likely to be influenced by factors outside of the control or influence of GB. |  | Y13 | 940.26 | 0 | 0
| Life Expectancy of Solution: | 20 |  |  | EES asset life is electrochemically limited by the number of charge/discharge cycles that the technology can sustain without severe performance degradation. The chemicals used in flow-cell batteries are highly reactive; with every cycle the chemically active parts pollute to some degree, such that over the course of time, performance suffers. In this respect, flow cells offer the greatest potential for longevity as the active parts can be replaced or refreshed to renew performance. As life depends on cycles, limiting the number of cycles necessary to provide upgrade deferment by a form of intelligent control may be necessary. Considering daily cycles used for peak lopping over one-quarter of a year, the various technologies would have calendar lives (determined from cycle numbers per year) of up to 15 years for lead-acid and up to 30 years for sodium metal-halide. We have assumed a lifetime of 20 years within our modelling. |  | Y14 | 940.26 | 0 | 0
| Totex (£): | 77267 |  |  | Calculated from capex plus NPV of opex |  | Y15 | 940.26 | 0 | 0
Merit Order | Disuption Factor (1-5): | 2 |  |  | Deployment requires suitable space to be available, which can be a premium, particularly in congested urban and suburban substations. Compared to reinforcement (e.g. the construction of new overhead lines or substations), planning processes should be reduced, although there may be additional complexities owing to the electrochemical nature of the units. |  | Y16 | 940.26 | 0 | 0
| Disruption Cost (£): | 2500 |  |  | Figure based on Disruption Factor (taken from Table 13.7 in the WS3 Report) |  | Y17 | 940.26 | 0 | 0
| Flexibility (1-5): | 3 |  |  | Most types of EES could be relocated or expanded in a modular manner as the need to peak lop changes over time. Given the interest in EES and the relatively limited supply capacity for utility-scale applications, availability will be subject to global markets. |  | Y18 | 940.26 | 0 | 0
| Cross Network Benefits Factor: | 2 |  |  | Solution is likely to provide a benefit to HV networks |  | Y19 | 940.26 | 0 | 0
Other Benefits | Impact on Fixed Losses (%): | 25% |  |  | This solution is will increase fixed losses as the round-trip efficiency of a storage unit is less than 100% - this differs by manufacturer and storage type. |  | Y20 | 940.26 | 0 | 0
| Impact on Variable Losses (%): | -15% |  |  | As DSR, this solution has the ability to reduce the losses down a circuit by reducing the peak demand (less current, therefore less heating loss). As this is the largest LV unit, it has the largest impact on LV losses.
| Impact on quality of Supply (%): | 0% |  |  | This solution is not expected to give any benefit to QoS
Year solution becomes available: |  | 2012 |  |  | Estimate - based on solutions being available for purchase (for trial)
Year data (on soln) is available: |  | 2012 |  |  | 0
Source of Data: |  | SGS
Smart Solution Relevance (WS3 Ph1) | Smart Solution Set: | smart
Focus:
Subset:

## Storage LV EES Small
Solution Overview | Representative Solution: | Energy Storage |  |  |  | Smart Variant | discount rate | 3.5%
| Variant Solution: | Electrical Energy Storage_LV connected EES - small |  |  |  |  | Y1 | 10000 | 0 | 0 | annual opex (per feeder)
| Description: | Electrical Energy Storage (EES) technologies (smaller-sized LV connected batteries, e.g. serving 1 or 2 residential properties) deployed on a network to either deliver the peak demand, or absorb high levels of generation at key times of the day/year. The charge cycles of EES can be tuned to local network conditions, but is ultimately a function of the capacity (MW and MWh) of the units. Storage size for this variant is 50kW; 100kWh. |  |  |  |  | y2 | 10000 | 0 | 0
|  | EHV | HV | LV | Comments |  | Y3 | 10000 | 0 | 0
Headroom Release (%) | Thermal Cable: |  |  | 0% | Determined in the Model (DM): In a similar vein to Residential DSR, this EES solution is deployed in a comprehensive 'bottom-up' manner, taking into account the magnitude and duration of the peak, and the capacity (MW and MWh) available of the storage unit. |  | Y4 | 10000 | 0 | 0
| Thermal Transformer: |  |  | 0% | As Thermal Cable, this is calcuated within the model, and based on the aggregated ouput of the types of loads that can be moved. |  | Y5 | 10000 | 0 | 0
| Voltage Head: |  |  | 0% | EES would typically be used to flatten peaks created by generation (e.g. high volts resulting from PV in the middle of the day or onshore windfarms under windy conditions) or load (e.g. low volts resulting from EVs at the early evening peak). |  | Y6 | 10000 | 0 | 0
| Voltage Leg: |  |  | 0% | Based on the thermal profiles calculated within the model - flattening of peak demand will reduce volt drops along the circuit, thereby improving voltage legroom. |  | Y7 | 10000 | 0 | 0
| Power Quality: |  |  | 0% | No modelled benefit (it is noted that the converter on the battery unit may provide some power quality support, but as the model has not been setup to consider PQ issues, analysis has not been carried out on this aspect of EES) |  | Y8 | 10000 | 0 | 0
| Fault Level: |  |  | -5% | EES can be made to 'look' like a generator to the network, feeding in fault current at the time of fault. As the storage unit sits behind power electronics, this effect is damped, but as this unit is medium sized it has been modelled as reducing FL headroom by 5%. |  | Y9 | 10000 | 0 | 0
Cost (£) | Capital: | 410000 |  |  | Costs have been based on average prices seen in trials for the size of unit provided in 'Description' above and scaled accordingly. The costs include the procurement of storage units, power electronics, connection infrastructure, and installation & commissioning works. |  | Y10 | 10000 | 0 | 0
| Operational Expenditure: | 10000 |  |  | Estimation of the annual cost of running communications to the devices. NB. The EES's energy costs have not been factored into this model, and are instead treated as a network loss. |  | Y11 | 10000 | 0 | 0
| NPV of Opex: | 184761 |  |  | Based on 20 year of annual operating expenditure @ 3.5% discount rate |  | Y12 | 10000 | 0 | 0
| Cost Curve Type: | 5 |  |  | In 2012, EES units are not readily available off-the-shelf, with typical lead-times of 6-18 months. This is about equivalent to the amount of time that should be allocated for pre-installation project and site preparation, fire, operation and safety procedures. LV units could be deployed in large volumes, accelerating the cost curve roll off. However, it is noted that storage is a global market and is likely to be influenced by factors outside of the control or influence of GB. |  | Y13 | 10000 | 0 | 0
| Life Expectancy of Solution: | 20 |  |  | EES asset life is electrochemically limited by the number of charge/discharge cycles that the technology can sustain without severe performance degradation. The chemicals used in flow-cell batteries are highly reactive; with every cycle the chemically active parts pollute to some degree, such that over the course of time, performance suffers. In this respect, flow cells offer the greatest potential for longevity as the active parts can be replaced or refreshed to renew performance. As life depends on cycles, limiting the number of cycles necessary to provide upgrade deferment by a form of intelligent control may be necessary. Considering daily cycles used for peak lopping over one-quarter of a year, the various technologies would have calendar lives (determined from cycle numbers per year) of up to 15 years for lead-acid and up to 30 years for sodium metal-halide. We have assumed a lifetime of 20 years within our modelling. |  | Y14 | 10000 | 0 | 0
| Totex (£): | 717761 |  |  | Calculated from capex plus NPV of opex |  | Y15 | 10000 | 0 | 0
Merit Order | Disuption Factor (1-5): | 2 |  |  | Deployment requires suitable space to be available, which can be a premium, particularly in congested urban and suburban substations. Compared to reinforcement (e.g. the construction of new overhead lines or substations), planning processes should be reduced, although there may be additional complexities owing to the electrochemical nature of the units. |  | Y16 | 10000 | 0 | 0
| Disruption Cost (£): | 2500 |  |  | Figure based on Disruption Factor (taken from Table 13.7 in the WS3 Report) |  | Y17 | 10000 | 0 | 0
| Flexibility (1-5): | 4 |  |  | Most types of EES could be relocated or expanded in a modular manner as the need to peak lop changes over time. Given the interest in EES and the relatively limited supply capacity for utility-scale applications, availability will be subject to global markets. |  | Y18 | 10000 | 0 | 0
| Cross Network Benefits Factor: | 2 |  |  | Solution is likely to provide a benefit to HV networks |  | Y19 | 10000 | 0 | 0
Other Benefits | Impact on Fixed Losses (%): | 15% |  |  | This solution is will increase fixed losses as the round-trip efficiency of a storage unit is less than 100% - this differs by manufacturer and storage type. |  | Y20 | 10000 | 0 | 0
| Impact on Variable Losses (%): | -5% |  |  | As DSR, this solution has the ability to reduce the losses down a circuit by reducing the peak demand (less current, therefore less heating loss). As this is the smallest LV unit, it has less of an impact on LV losses.
| Impact on quality of Supply (%): | 0% |  |  | This solution is not expected to give any benefit to QoS
Year solution becomes available: |  | 2012 |  |  | Estimate - based on solutions being available for purchase (for trial)
Year data (on soln) is available: |  | 2012 |  |  | 0
Source of Data: |  | SGS
Smart Solution Relevance (WS3 Ph1) | Smart Solution Set: | smart
Focus:
Subset:

## RTTR_EHV_OHL(GUS)
Solution Overview | Representative Solution: | RTTR |  |  |  | Smart Variant | discount rate | 3.5%
| Variant Solution: | RTTR for EHV OH lines (GUS) |  |  |  |  | Y1 | 0 | 0 | 0 | annual opex (per feeder)
| Description: | The use of measurement and ambient forecasting data to predict the rating (and hence current carrying capacity) of assets in a real-time mode. This variant considers RTTR for EHV overhead line circuits. |  |  |  |  | y2 | 500 | 0 | 0
|  | EHV | HV | LV | Comments |  | Y3 | 500 | 0 | 0
Headroom Release (%) | Thermal Cable: | 10% | !% | !% | The benefits notes here are indicative of what may be achieved in collaboration with an ANM. Any implementation will need a full site survey to identify real benefits. Furthermore it is likely to be available linked only to new generation connections or DSR. Much further work is required to identify how frequently RTTR OHL can actually be deployed on a network. Furthermore, full deployment of RTTR OHL may not be available until a full review of current ESQCR regulations are conducted. For these reasons we do not expect wide scale deployment of RTTR OHL in the next few years. |  | Y4 | 500 | 0 | 0
| Thermal Transformer: | 0% | !% | !% | No benefit expected |  | Y5 | 500 | 0 | 0
| Voltage Head: | 0% | !% | !% | No benefit expected |  | Y6 | 500 | 0 | 0
| Voltage Leg: | 0% | !% | !% | No benefit expected |  | Y7 | 500 | 0 | 0
| Power Quality: | 0% | !% | !% | No benefit expected |  | Y8 | 500 | 0 | 0
| Fault Level: | 0% | !% | !% | No benefit expected |  | Y9 | 500 | 0 | 0
Cost (£) | Capital: | 16600 |  |  | Estimate based on the purchase and installation of monitoring devices (e.g. conductor mounted measurement devices) at key points along the overhead line circuit. |  | Y10 | 500 | 0 | 0
| Operational Expenditure: | 0 |  |  | No ongoing opex cost assumed (NB. Costs of weather monitoring are factored into the associated Enabler) |  | Y11 | 500 | 0 | 0
| NPV of Opex: | 0 |  |  | Based on 20 year of annual operating expenditure @ 3.5% discount rate |  | Y12 | 500 | 0 | 0
| Cost Curve Type: | 3 |  |  | Assume a reduction in costs as solution volumes increase |  | Y13 | 500 | 0 | 0
| Life Expectancy of Solution: | 15 |  |  | At present, asset life is something of an unknown. The equipment is designed to act in a “fit and forget” manner without the requirement for ongoing maintenance. The life of the equipment for overhead line dynamic thermal ratings solutions (i.e. “power donuts”, current transformers etc.) is assumed to be 15 years; |  | Y14 | 500 | 0 | 0
| Totex (£): | 16600 |  |  | Calculated from capex plus NPV of opex |  | Y15 | 500 | 0 | 0
Merit Order | Disuption Factor (1-5): | 2 |  |  | Low disruption as the devices can be connected to the network with minimal of impact / outages |  | Y16 | 500 | 0 | 0
| Disruption Cost (£): | 2500 |  |  | Figure based on Disruption Factor (taken from Table 13.7 in the WS3 Report) |  | Y17 | 500 | 0 | 0
| Flexibility (1-5): | 4 |  |  | Devices could easily be moved from one circuit to another within their life expectancy |  | Y18 | 500 | 0 | 0
| Lead Time | 6 |  |  | Typically 6 months lead time for acquisition
| Cross Network Benefits Factor: | 0 |  |  | No benefit expected |  | Y19 | 500 | 0 | 0
Other Benefits | Impact on Fixed Losses (%): | 0% |  |  | No benefit expected |  | Y20 | 500 | 0 | 0
| Impact on Variable Losses (%): | 20% |  |  | Solution is expected to increase the variable losses (I²R) as more current is pushed down the circuit. The exact increase depends on the magnitude and duration of operating at these higher currents.
| Impact on quality of Supply (%): | 1% |  |  | A marginal benefit to QoS as this solution may provide additional monitoring of the network, potentially assisting DNOs in identifying faults or fault locations.
Year solution is available: |  | 2015 |  |  | Estimate - based on CLNR field trial
Year data (on soln) is available: |  | 2015 |  |  | Estimate - based on CLNR field trial
Source of Data: |  | CLNR, Workstream 2, WPD 132kV, SP Dynamic Rating
Smart Solution Relevance (WS3 Ph1) | Smart Solution Set: | Smart D-Networks 3
| Focus: | Plant & Systems reliability, failure mode detection
| Subset: | Dynamic ratings for all plant types and multi element circuits

## RTTR_HV_OHL(GUS)
Solution Overview | Representative Solution: | RTTR |  |  |  | Smart Variant | discount rate | 3.5%
| Variant Solution: | RTTR for HV OH lines (GUS) |  |  |  |  | Y1 | #REF! | 0 | 0 | annual opex (per feeder)
| Description: | The use of measurement and ambient forecasting data to predict the rating (and hence current carrying capacity) of assets in a real-time mode. This variant considers RTTR for HV overhead line circuits. |  |  |  |  | y2 | 500 | 0 | 0
|  | EHV | HV | LV | Comments |  | Y3 | 500 | 0 | 0
Headroom Release (%) | Thermal Cable: | !% | 3% | !% | The benefits here are indicative of what may be achieved in collaboration with an ANMnly. Any implementation will need a full site survey to identify real benefits. Furthermore it is likely to be available linked only to new generation connections or DSR. Much further work is required to identify how frequently RTTR OHL can actually be deployed on a network. Furthermore, full deployment of RTTR OHL may not be available until a full review of current ESQCR regulations are conducted. For these reasons we do not expect wide scale deployment of RTTR OHL in the next few years. |  | Y4 | 500 | 0 | 0
| Thermal Transformer: | !% | 0% | !% | No benefit expected |  | Y5 | 500 | 0 | 0
| Voltage Head: | !% | 0% | !% | No benefit expected |  | Y6 | 500 | 0 | 0
| Voltage Leg: | !% | 0% | !% | No benefit expected |  | Y7 | 500 | 0 | 0
| Power Quality: | !% | 0% | !% | No benefit expected |  | Y8 | 500 | 0 | 0
| Fault Level: | !% | 0% | !% | No benefit expected |  | Y9 | 500 | 0 | 0
Cost (£) | Capital: | 12300 |  |  | Estimate based on the purchase and installation of monitoring devices (e.g. conductor mounted measurement devices) at key points along the overhead line circuit. |  | Y10 | 500 | 0 | 0
| Operational Expenditure: | 0 |  |  | No ongoing opex cost assumed (NB. Costs of weather monitoring are factored into the associated Enabler) |  | Y11 | 500 | 0 | 0
| NPV of Opex: | 0 |  |  | Based on 20 year of annual operating expenditure @ 3.5% discount rate |  | Y12 | 500 | 0 | 0
| Cost Curve Type: | 3 |  |  | Assume a reduction in costs as solution volumes increase |  | Y13 | 500 | 0 | 0
| Life Expectancy of Solution: | 15 |  |  | At present, asset life is something of an unknown. The equipment is designed to act in a “fit and forget” manner without the requirement for ongoing maintenance. The life of the equipment for overhead line dynamic thermal ratings solutions (i.e. “power donuts”, current transformers etc.) is assumed to be 15 years; |  | Y14 | 500 | 0 | 0
| Totex (£): | 12300 |  |  | Calculated from capex plus NPV of opex |  | Y15 | 500 | 0 | 0
Merit Order | Disuption Factor (1-5): | 2 |  |  | Low disruption as the devices can be connected to the network with minimal of impact / outages |  | Y16 | 500 | 0 | 0
| Disruption Cost (£): | 2500 |  |  | Figure based on Disruption Factor (taken from Table 13.7 in the WS3 Report) |  | Y17 | 500 | 0 | 0
| Flexibility (1-5): | 4 |  |  | Devices could easily be moved from one circuit to another within their life expectancy |  | Y18 | 500 | 0 | 0
| Lead Time | 6 |  |  | Typically 6 months lead time for acquisition
| Cross Network Benefits Factor: | 0 |  |  | No benefit expected |  | Y19 | 500 | 0 | 0
Other Benefits | Impact on Fixed Losses (%): | 0% |  |  | No benefit expected |  | Y20 | 500 | 0 | 0
| Impact on Variable Losses (%): | 20% |  |  | Solution is expected to increase the variable losses (I²R) as more current is pushed down the circuit. The exact increase depends on the magnitude and duration of operating at these higher currents.
| Impact on quality of Supply (%): | 0.01% |  |  | A marginal benefit to QoS as this solution may provide additional monitoring of the network, potentially assisting DNOs in identifying faults or fault locations.
Year solution is available: |  | 2015 |  |  | Based on CLNR
Year data (on soln) is available: |  | 2015 |  |  | Based on CLNR
Source of Data: |  | CLNR, SSE T1 33kV, Workstream 2, SP Flexible Networks, SSE NINES, UKPN Flexible plug and play
Smart Solution Relevance (WS3 Ph1) | Smart Solution Set: | Smart D-Networks 3
| Focus: | Plant & Systems reliability, failure mode detection
| Subset: | Dynamic ratings for all plant types and multi element circuits